## Slide 1: UV Disinfection Design and Procurement Guidelines
Andrea Tom, PE

## Slide 2: New UV Equipment Steps
Understand Influent and Effluent Water Quality
Establish Design Criteria
Proper Sizing
Procurement
Design Considerations
Construction, Start-up, and Testing

## Slide 3: Understanding Water Quality and Establishing Design Criteria
Notes: They are interrelated

## Slide 4
Notes: Collimated beam is like a UV response testing
When get to 10% increase in UVT, you can approx. cut the lamps in half!

## Slide 5
Notes: It’s always site-specific. This particular client had a lot of data and were very risk averse.
Can change seasonally: UVT, TSS, undisinfected bacteria counts

## Slide 6
Notes: Collimated beam is like a UV response testing
When get to 10% increase in UVT, you can approx. cut the lamps in half!

## Slide 7: Proper Sizing

## Slide 8: Tailoring the System to Your Needs
Chart: UV Dose (mJ/cm2)
| 0 | 5 | 10 | 20 | 40 | 80
2015 CB | 0 | 0.57793 | 1.5127 | 2.7659 | 3.243 | 3.669
2018 CB | 0 | 0.4956 | 1.7434 | 2.6812 | 3.2553 | 3.8573
98th Percentile Enterococcus, Geomean, 0.5 log SF | 3 | 3
Determine required Enterococcus or E. Coli log inactivation
1
Plot Collimated Beam Results
2
Determine UV dose and organism sensitivity
3
Notes: It’s always site-specific. This particular client had a lot of data and were very risk averse.
Can change seasonally: UVT, TSS, undisinfected bacteria counts

## Slide 9: Procurement

## Slide 10: Pre-selection versus Hard Bid
Opportunity to account for non-cost impacts
Designing around a single manufacturer can reduce construction costs
SDs get reviewed during design
Minimizes coordination changes during construction

## Slide 11: Pre-selection Process
RFP development
  Technical requirements and scope
  UV system testing options (hydraulics, harmonic, elevated TSS testing, etc)
  Delegated design
  Compensation for submittal development
  Approach to spare parts and bid price escalation
RFP
RFP evaluation – NPV and non-cost weights
Notice of Award/Letter of Intent to selected UV manufacturer
Contract is still between the Contractor and the UV manufacturer

## Slide 12: Procurement Lessons Learned
Discuss and agree on start-up and testing requirements.
Vet out approved vendors.
Engage operational staff for their input!
Redundancy

## Slide 13: Design Considerations

## Slide 14: UV System Design Considerations
Headloss
TCEQ Requirements
  Spare part storage
  Redundancy
  Channel drainage
Controls: Automatic flow and water quality paced PLC control system
Alarms
Flow control: finger weir versus modulating weirs
Flow split and flow measurement
Environmental controls for panels
Sampling points
Cable routing and lengths
Channel Covers
Future expansion
Notes: Environmental controls

## Slide 15: Design – Other Considerations
Secondary clarifier launder covers to reduce algae formation
  Installing launder covers under on-going projects.
Use of ferric for upstream processes
Additional headloss from future upstream processes
Impact of process upsets
Power

## Slide 16: UV Facility – Value Engineering (VE)
Building
  Pre-Engineered Metal Building
    An enclosed electrical room and designed to allow for the full enclosure of the entire structure in the future
  Canopy over the UV disinfection facility as bid alternate
Flowmeter Locations
    Moved from yard valve vault vs in Channel
Large diameter piping materials
Electrical Building
  PDCs inside electrical building vs outside
  FRP Prefabricated building
ELECTRICAL
EFF SAMPLE
VE
VE

## Slide 17: Construction and Testing/Startup

## Slide 18: Construction and MOPO Lessons Learned
Keep lines of communication open between all parties.
Have clear sequencing discussions.
Know the minimum equipment performance needed at the process, if bypass is not possible.
Establish and agreed upon a game plan before critical demolitions occur.
Notes: 1- what needs to be in operation at all times? How long can you shut the plant down? Do you have an EQ Basin? Where is power coming from if you are transferring from existing power?

## Slide 19: Testing and Startup Lessons Learned
Identify agencies to notify in advance before any sampling begins.
Closely review manufacturer’s performance testing plans and confirm responsibilities of all parties—especially when third parties are involved.
Understand the schedule and impacts from any burn-in requirements or potential undisinfected discharging.
Establish a clear chain of custody for sampling and lab testing.

## Slide 20: Questions

## Slide 21: Thank You!
Kaitlin Allen
Brian Hilts
CDM Smith Project Team
Acknowledgements
Andrea Tom
tomam@cdmsmith.com
My Contact Information