## Slide 1: Advanced Thermal Processes of Biosolids
TEXAS ASSOCIATION OF CLEAN WATER AGENCIES
MARCH 27, 2026

## Slide 2: EPA agrees with our published research findings
Notes: Published research findings are a project we did Minnesota pollution control agency aligns with

## Slide 3: Agenda
SCWO Technology Update
Gasification Technology Update
Pyrolysis Technology Update
Full Scale Capacity Comparison

## Slide 4: Supercritical Water Oxidation

## Slide 5: Supercritical Water Oxidation
Technology Overview
As pressure increase, water temp increases beyond the boiling point
Beyond critical point, organic matter rapidly dissolve and becomes simple molecules
With air/O2, organics are fully oxidized
Peak temp in SCWO is not hot enough to produce NOx or SOx
Not a combustion technology by EPA

## Slide 6: Technology overview/PFD
Liquid
Biosolids
Screw Press
10-15%
Slurry
Water
Minerals
Strain Press
CO2/Air
Air
Sludge Pre-Treatment
Energy
Sludge Grinder
Screenings
Filtrate
Polymer
Energy
Co-Fuel

## Slide 7: 374Water Status
Location | Equipment | Size (wtpd) | Year Demonstrated
City of Orlando, FL | AirSCWO 6 | 4.5 | March – June 2025
Orange County Sanitation District, CA | AirSCWO 6 (Hazen) | 6 | 2026
City of Olathe, KS | AirSCWO 6 (Hazen) | 4.92 | 2027
No installations yet, all piloting/demonstration

## Slide 8: Pilot Testing Results
Results from 374Water Presentation at Florida Remediation Conference Nov 4, 2025

## Slide 9: City of Olathe, KS – SCWO Pilot
Cedar Creek WWTP – 12.5 mgd after current expansion
Landfill disposal of biosolids going away​
$113M to transition to Class B land application(2024 Cedar Creek WWTP Expansion Plan)​
$5.8M KDHE Emerging Contaminate Grant Funding ​
Developed system since 2013 at Duke University​
Bill and Melinda Gates Foundation Funding​
AirSCWO 6 Unit currently operational in Michigan​
Leader in the market for SCWO treatment of biosolids​

## Slide 10: Olathe SCWO

## Slide 11: “Future” of SCWO – Full Scale and Piloting
Only the 1 wtpd unit will be available for piloting moving forward

## Slide 12: Gasification and Pyrolysis

## Slide 13: Gasification/Pyrolysis followed by Thermal Oxidation
Destruction Technology
Parameter | Incineration | Gasification | Pyrolysis
Temperature (ºF) | 1,650-2,000 | 1,100-1,800 | 390-1,100
O2 Supply | > Stoichiometric (Excess Air) | > Stoichiometric (Limited Air) | None
By-products | Flue Gas (CO2, H2O) and Ash | Syngas (H2, CO) and Ash | Pyrolysis Gas, Oil, Tars, and Char
Combustion | Complete combustion of organics | No combustion due to limited or no oxygen | 
Not an incineration process
Gasification/Pyrolysis is a thermochemical process use intense heat to decompose organic materials.

## Slide 14: Gasification
Ecoremedy
Earthcare
Pyrocal

## Slide 15: State of knowledge regarding PFAS fate before WRF #5107
Drying
+
Gasification/Pyrolysis
+
Thermal Oxidation
Sludge/
Biosolids In
Biochar/
Inert
Water In
Water Out
Air In
Air Out
PFAS
PFAS, yes
PFAS
PFAS?
Three data points show N/D,
All Vendors:
Ecoremedy
Bioforcetech
Chartech

## Slide 16: PFAS Fate in Edmonds Gasification Facility

## Slide 17: PFAS fate in Edmonds Gasification Facility with GAC and RTO

## Slide 18: Ecoremedy
Installations
Location | Equipment | Size (dtpd) | Year Built | Operational Status
Edmond, WA | ECR-542 | 11.0 | 2023 | Operational
Derry Township, PA | ECR-742 | 14.0 | 2025 | Commissioning Q1 2026
Edmond, WA
Derry Township, PA

## Slide 19: Earthcare
Gasification
System Information
Tripple Pass drying system, gasifier system coupled with thermal oxidizer
One train size is 40 dtpd
Have facilities in the Midwest for cow manure

## Slide 20: Earthcare
Installations
Earthcare has other facilities under construction
Location | Equipment | Size (dtpd) | Year Built | Operational Status
Bethel, PA Merchant facility | 50% sludge/biosolids 50% Chicken litter and other material | Two trains @ 80 dtpd total | 2024 | Operational

## Slide 21: Pyrocal
Gasification
Australia-Based
Drying and pyrolysis system coupled with thermal oxidation
Started in 2016
First installation is Logan Water (Australia) in 2022 with new generation in 2023
Pyrocal offers two (2) difference size
  CCT-12 (Up to ~1,300 dry tons/year)
  CCT-20 (Up to ~3,800 dry tons/year)

## Slide 22: Pyrocal (Gasification)
System Information and Installations
Pyrocal has eight (8) more installations operational since 2014 and later, treating rice hull, walnuts etc.
Location | Equipment | Size (dtpd) | Year Built | Operational Status
Loganholme, Australia | 2xCCT20 | ~32.0 | 2019 – Stable in 2022 | Operational
Victoria, Canada | CCT20 | ~16.0 | 2026/2027 | Under Construction

## Slide 23: Pyrolysis
Pyreg
AquaGreen

## Slide 24: Pyreg (Pyrolysis)
Pyrolysis coupled with thermal oxidizer
German company: opened offices in Maine
Pyreg system can be configured with different dryers, but recently coupled with belt dryer (Stella) and Berlie Falco as EPC from Quebec.
Pyrolyzer operates between 500 ºF to 1,200 ºF and residence time between 5 to 30 minutes
Two (2) sizes offering
  PX-500 (up to 1,000 dry tons annually) = 2.7 dtpd
  PX-1500 (up to 3,000 dry tons annually) = 8.2 dtpd
Energy recovery as hot water at 205 ºF
PFAS and other contaminants of concerns (CECs) removal
Automated system control for Pyrolysis system
Zero production of tars or bio-oil

## Slide 25: Pyreg System installations
PX-750 is no longer in the equipment list provided by Pyreg
Location | Equipment | Size (dtpd) | Year Built | Operational Status
Ephrata, PA | PX-500 | 2.8 | 2025 | Under Commissioning
Silicon Valley Water Commission, CA | PX-500 | 1.0 | 2017-2022 | Replaced
Tabor, Czech Republic | PX-1500 | ~5 | Q4 2025 | Under Commissioning
Sydney, Australia | 2 PX-1500 | ~11.5 | Q1 2026 | Under Construction
Kleve, Germany | PX-750 |  | 2022 | Commissioned
Lorsbach, Germany | PX-750 |  | 2021 | Commissioned
Trutnov, Czech Republic | PX-500 | ~ 3 | 2020 | Commissioned
Hammenhog, Sweden | PX-500 | ~ 3 | 2019 | Commissioned
Homburg, Germany | PX-500 | ~3 | 2016 | Commissioned
Unkel, Germany | PX-500 | ~3 | 2015 | Commissioned

## Slide 26: Pyreg Installations
Lorsbach, Germany
Kleve, Germany
Silicon Valley, CA

## Slide 27: Aquagreen (Pyrolysis)
Danish/Denmark based company – Represented by Alfa Laval in the USA
Steam drying and pyrolysis coupled with thermal oxidation
Started 2016, offering commercial systems since 2020
Superheated steam drying (248-392 ºF) for 2 hours
Pyrolysis at 1,200 ºF for 20 minutes
Two system (HECLA) sizes available for pyrolysis
  Series 1000  ~2.6 dtpd
  Series 1500  ~4 dtpd.
Recover thermal energy as hot water (~160 ºF)
Potential to be Autogenous
Eliminate PFAS, Pharmaceuticals, microplastics and PAHs
Natural gas or liquid petroleum gas (LPG) is required for start-up

## Slide 28: HECLA Configuration/Operation
1: You feed biosolids – digested or not, 18+% dry matter into the dryer
2: You dry biosolids with super-heated steam at 120 - 200oC/ 250 - 400oF for 2 hours
3: You condense excess steam
4: You pyrolyze at 650oC / 1,200oF for 10 minutes
5: You combust the pyrolysis gas at 900oC/ 1650oF
6: Your end-product is biosolids biochar
7: You treat the flue gas in the wet scrubber

## Slide 29: Aquagreen
Location | Equipment | Size (dtpd) | Year Built | Operational Status
Odsherred Forsyning (Denmark) | HECLA 1000 | 2.6 | 2022 | Operational
Vandcenter SYD (Denmark) | HECLA 1000 | 2.6 | 2023 | Operational
Lemvig Vand (Denmark) | HECLA 1000 | 2.6 | 2025 | Operational
Tarnby Forsyning (Denmark) | HECLA 1500 | 4.0 | 2025 | Operational
VASYD (Sweden) | HECLA 300 | 1.0 | 2024 | Operational
Roslagsvatten (Sweden) | HECLA 1500 | 4.0 | Q1 2026 | Under Commissioning

## Slide 30: Technology Capacity Comparison
SCWO
Gasification
Pyrolysis

## Slide 31: Solids Production based on Annual Average Influent Flow
Chart: Annual Average Influent Flow (mgd)
| 0 | 5 | 10 | 20 | 40 | 80 | 120 | 200
PS+WAS No Stabilization | 0 | 5.2539 | 10.5079 | 21.0158 | 42.0316 | 84.0631 | 126.0947 | 210.1579
PS+WAS With Stabilization | 0 | 3.2322 | 6.4644 | 12.9288 | 25.8575 | 51.715 | 77.5726 | 129.2876
WAS Only No Stabilization | 0 | 4.295 | 8.5899 | 17.1798 | 34.3596 | 68.7192 | 103.0788 | 171.798
Influent Characteristics:
250 mg/L BOD
250 mg/L TSS
10 day Aerobic SRT

## Slide 32: Current Capacity of PFAS Removal Technologies from Biosolids
Chart: Annual Average Influent Flow (mgd)
| 0 | 5 | 10 | 20 | 40 | 80 | 120 | 200
PS+WAS No Stabilization | 0 | 5.2539 | 10.5079 | 21.0158 | 42.0316 | 84.0631 | 126.0947 | 210.1579
PS+WAS With Stabilization | 0 | 3.2322 | 6.4644 | 12.9288 | 25.8575 | 51.715 | 77.5726 | 129.2876
WAS Only No Stabilization | 0 | 4.295 | 8.5899 | 17.1798 | 34.3596 | 68.7192 | 103.0788 | 171.798
Gasification | 5.5 | 40 | 80
Pyrolysis | 1 | 11.5
SCWO | 0.5 | 11
Gasification
Pyrolysis
SCWO

## Slide 33: Current Capacity of PFAS Removal Technologies from Biosolids
Chart: Annual Average Influent Flow (mgd)
| 0 | 5 | 10 | 20 | 40 | 80 | 120 | 200
PS+WAS No Stabilization | 0 | 5.2539 | 10.5079 | 21.0158 | 42.0316 | 84.0631 | 126.0947 | 210.1579
PS+WAS With Stabilization | 0 | 3.2322 | 6.4644 | 12.9288 | 25.8575 | 51.715 | 77.5726 | 129.2876
WAS Only No Stabilization | 0 | 4.295 | 8.5899 | 17.1798 | 34.3596 | 68.7192 | 103.0788 | 171.798
Gasification | 5.5 | 40 | 80
Pyrolysis | 1 | 11.5
SCWO | 0.5 | 3.3 | 11
Gasification
Pyrolysis
SCWO

## Slide 34: Current Capacity of PFAS Removal Technologies from Biosolids
80 to 120 mgd
5.5 to 80 dtpd
Largest available capacity units
Overall 80% to 99% PFAS removal
Complete PFAS destruction/ removal from residual solids
Needs dewatering and drying
Multiple complicated systems similar to rotary drum dryer
Gasification
10 to 20 mgd
1 to 11.5 dtpd
Smaller capacity units
Overall 80% to 99% PFAS removal
Complete PFAS destruction/ removal from residual solids
Needs dewatering and drying (belt dryer/stream or paddle dryer)
Pyrolysis
<5 mgd (up to 20 mgd planned)
0.5 dtpd (up to 11 dtpd planned)
Thickening / Dewatering to 8 -12%
One unit process
  Air compressor, sludge pumps and piping
  No separate dryer system, steam, burner, ductwork and material transfer conveyors
Undetectable PFAS in minerals and exhaust
Lowest estimated disposal costs
Scale up ability not yet proven
SCWO