## Slide 1: Addition by Subtraction – Expanding and Simplifying Lewisville’s Aged Secondary Treatment Process
November 14, 2025
Katelyn Hearon, City of Lewisville
Joel Cantwell, HDR

## Slide 2
1
Existing Facilities Overview
2
Master Plan (2020)
3
Secondary Treatment Expansion Project (Current)
4
Questions

## Slide 3
1
Existing Facilities Overview

## Slide 4: City of Lewisville
Population of 137,000
Growing at approx. 1.5% annually
Treat our own water and wastewater
Prairie Creek WWTP
  Original 1950 (1.75 mgd)
  Various expansions (1974, 1987, 1995, 2004, 2013)
  Current permit for 12 mgd AADF / 30 mgd P2H
Prairie Creek WWTP

## Slide 5: City of Lewisville Collection System
(18)
(17 miles)
(380 miles)

## Slide 6
Admin/Lab
Influent PS
Screening
Grit Removal
Filters
Chlorine Contact
Plant I
Plant II
Plant III

## Slide 7: The Prairie Creek WWTP process includes 3 parallel secondary treatment plants
Parameter | Value
AADF | 12 mgd
BOD | 10 mg/L
TSS | 15 mg/L
TPDES Permit Limits

## Slide 8
  Capacity expansion needed by 2027
  Potential ammonia limits this decade
  Potential future phosphorus limits
  Desire to address operational complexity of 3 plants
Chart: Year
| 2020 | 2050
Adjusted Flow Projections Based on Current Flow and Estimated 2050 Buildout (HDR) | 9.6 | 19.6
Capacity and process challenges are on the horizon

## Slide 9
2
Master Plan

## Slide 10: Master Plan Elements
Build-out planning criteria
Condition, process, and hydraulic assessments
Overall treatment process strategy
Improvements for each unit process
Short- and long-term CIP
Alternatives:
  Conventional activated sludge (3-stage BNR)
  Membrane bioreactors (MBR)
  Aerobic granular sludge (AGS)
Plant III near end of useful life
All aeration basins are shallow (12’ SWD)
Total capacity with full nitrification <11 mgd

## Slide 11: 3-Stage BNR Conventional Activated Sludge

## Slide 13: Membrane Bioreactor

## Slide 15: Aerobic Granular Sludge (AquaNereda®)

## Slide 17: Decision modeling helped the City select the preferred approach

## Slide 18: Conventional 3-stage BNR was selected

## Slide 19: Master Plan was finalized in 2020
The first major project was aeration basin expansion

## Slide 20
3
Aeration Basin Expansion Project

## Slide 21: The Project Modernizes the Plant’s Secondary Treatment
Aeration Basins No. 5-8 (16-mgd)
Aeration Basin Splitter Structure
Secondary Clarifier Splitter Structure
Future Rehab Basins No. 1-4 (derate to 4-mgd)
Blower Building
RAS Pump Station Rehab

## Slide 22: Aeration Basin Splitter Structure (8-way flow split)
Influent from Headworks
RAS

## Slide 23: Aeration Basins No. 5-8
Anoxic Zones
Aerobic Zones (tapered)

## Slide 24: Aeration Basins No. 5-8
Anoxic Zones
Mixed Liquor Return

## Slide 25
Aeration Basins 5-8
Aeration Basins 1-4 (Future Rehab)
Secondary Clarifier Splitter Structure

## Slide 26: Secondary Clarifier Splitter Structure
36” Motorized Plug Valve
36” Mag Meter

## Slide 27
No. 1
No. 4
No. 3
No. 2
Secondary Clarifier Splitter Structure
RAS Pump Station

## Slide 28: Blower Building
Blowers No. 1-4
Blowers No. 5-8 (Future)

## Slide 29: Blower Building
Inlet Filter/Silencer
36” Air Header

## Slide 30: RAS Pump Station
Replace all pumps, valves, and piping
Replace electrical and add VFDs
Add automated valves and meters for wasting sludge

## Slide 31: RAS Pump Station – minimum clearance prevented costly building renovations
7’

## Slide 32: Key takeaways
Strive to simplify operations while increasing reliability
Reuse existing infrastructure where possible
Evaluate innovative technologies but conventional approaches may win out (use decision modeling)
Consider how to maintain treatment capacity during construction

## Slide 33: Questions?
Katelyn Hearon
Assistant Director, Public Services
City of Lewisville
khearon@cityoflewisville.com
972-219-3509
Joel Cantwell, PE
Vice President
HDR
joel.cantwell@hdrinc.com
972-960-4440