## Slide 1
TACWA | March 27, 2026
A case study panel discussion
Creative operational strategies for rapid service area growth

## Slide 2: UTRWD Northeast Region
Riverbend WRP (4 mgd AADF Capacity)
1.47 mgd -> 3.54 mgd AADF
2003 -> 2026
Doe Branch WRP (4 mgd AADF Capacity)
2.05 mgd -> 5.69 mgd AADF
2016 -> 2026
Expansion to 12 mgd in construction

## Slide 3: Doe Branch Expansion to 4 mgd completed in 2022
Influent lift station includes transfer pumps to RBWRP

## Slide 4: What has the growth in the Northeast Region Looked like for UTRWD?
01
Jeff Mlak, Upper Trinity Regional Water District Operations Manager

## Slide 5: UTRWD operations follows growth
 | ‘16 |  |  |  | ‘20 |  |  |  |  | ‘26 |  |  |  |  |  |  | ‘50 | 
Population Growth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Treatment Capacity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Treatment Facility Projects |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Model Build |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
NE Regional WR System Budget |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
35,236
119,928
439,000
4.94 mgd
10.0 mgd
30.3 mgd
DB Ph 1
RB Ph 3
DB Ph 2
PN Ph 2
DB
Ph 3
PN
Ph 3
RB
Ph 4
DB
Ph 4
$4.2 M
8 People
0.84 BG
$8.3 M
13 People
2.0 BG
$20.0 M (+476% from 2016)
20 People (+250% from ‘16)
3.9 BG (+464% from ‘16)
?
Design

## Slide 6: Actual waste load increased from phase 2
BOD Increased from ~220 mg/l to 300 mg/l
Influent Ammonia from ~30 mg/l to 35 mg/l
Ph 2 Construction
Ph 2 Construction

## Slide 7: Doe Branch Flows (365-day average)
Transfer to RBWRP

## Slide 8: High performance under stress
Parameter | Design | 2025 Actual | % of Design | Eff. Performance
Flow | 4.0 mgd | 5.97 mgd | 149% | N/A
CBOD | 6,005 lbs/day | 11,462 lbs/day | 191% | 2.44 mg/L
TSS | 5,595 lbs/day | 7,339 lbs/day | 76% | 2.5 mg/L
Ammonia | 1,001 lbs/day | 1,871 lbs/day | 187% | 0.29 mg/L
Phosphorus | 200 lbs/day | 248 lbs/day | 124% | 0.165 mg/L

## Slide 9: How are you operating the plant to consistently maintain excellent treatment with the extreme changes in flow and load?
02
Joe Thompson, UTRWD Operations Supervisor

## Slide 10: RAS conditioning has been effective

## Slide 11: SBR Inspired operation lowers P and N, adds Alkalinity
Chart: mg/L
| NH3-N | TP | Alkalinity
Before | 500 | 300 | 0
After | 5 | 30 | 50

## Slide 12: What is happening? Why is this working so well?
03
Anton Dapcic, Carollo TX Wastewater Practice Lead

## Slide 13
Effluent TP (mg/L)
Effluent Alkalinity (mg/L as CaCO₃)
RAS TSS (mg/L)
Effluent NO3-N (mg/L)
Sludge Volume Index (mL/g)

## Slide 14: The Phase 3 Expansion includes RAS fermentation
OXIC
ANA
ANX
Doe Branch WRP Phase 3 (8 mgd AADF)
ANX
RAS
WAS
MLR
Wastewater

## Slide 15: Questions for the panel?

## Slide 17: Are you operating in a similar way at Riverbend and Peninsula?
04
Joe / Jeff

## Slide 18: Are there odor control or other benefits to this strategy?
05

## Slide 19: Has dewatering quality and consistency improved or been challenged by operating this way?
06